April 29, 2019

Lead in Drinking Water – Public and Nonpublic Schools

IMPORTANT NOTICE:  ELEVATED WATER SAMPLE RESULT(S)

The Maryland School for the Blind

ELEVATED LEAD WATER SAMPLE RESULT(S)

All Maryland public and nonpublic schools are required to sample all drinking water outlets for the presence of lead pursuant to the Code of Maryland Regulations.

On 3/23/19, 44 lead water samples were collected from Thompson Hall, Sippel Pool, and the Brick Rancher. Of these lead water samples, 6 had levels of lead exceeding the action level of 20 parts per billion (ppb) for lead in drinking water in school buildings. The elevated lead results from the samples collected at these three Buildings were as follows:

Thompson 		W3 Right Sink 				32.3 PPB

W9 Right Sink 				22.2 PPB

Sippel Pool		Girl’s Bathroom last sink on the left 		24.4 PPB

Boy’s Bathroom First sink on the Right 	20.6 PPB

Drinking Fountain 				38.9 PPB

Brick Rancher	Basement Laundry Sink 			196 PPB

ACTION LEVEL (AL)

The AL is 20 ppb for lead in drinking water in school buildings. The AL is the concentration of lead which, if exceeded, triggers required remediation.

HEALTH EFFECTS OF LEAD

Lead can cause serious health problems if too much enters your body from drinking water or other sources. It can cause damage to the brain and kidneys, and can interfere with the production of red blood cells that carry oxygen to all parts of your body. The greatest risk of lead exposure is to infants, young children, and pregnant women. Lead is stored in the bones and it can be released later in life. During pregnancy, the fetus receives lead from the mother’s bones, which may affect brain development. Scientists have linked the effects of lead on the brain with lowered IQ in children. Adults with kidney problems and high blood pressure can be affected by low levels of lead more than healthy adults.

SOURCES OF HUMAN EXPOSURE TO LEAD

There are many different sources of human exposure to lead. These include: lead-based paint,

lead-contaminated dust or soil, some plumbing materials, certain types of pottery, pewter, brass fixtures, food, and cosmetics, exposure in the work place and exposure from certain hobbies, brass faucets, fittings, and valves. According to the Environmental Protection Agency (EPA), 10 to 20 percent of a person’s potential exposure to lead may come from drinking water, while for an infant consuming formula mixed with lead-containing water this may increase to 40 to 60 percent.

IMMEDIATE ACTIONS TAKEN

All six outlets listed above were shut down within 24 hours from the time we received the results and do not use signage put in place. In addition an e-mail was sent out notifying all staff of initial results as we were receiving them.

NEXT STEPS

Thompson 		W3 Right Sink

Replaced Faucet and Supplies / Re-tested and Passed at 8.1 PPB

W9 Right Sink

Replaced Faucet and Supplies / awaiting test results

Sippel Pool		Girl’s Bathroom last sink on left

Replaced Faucet and Supplies / Re-tested and Passed at 11.9 PPB

Boy’s Bathroom first sink on Right

Replaced Faucet and Supplies / Re-tested and Passed at 19.2 PPB

Drinking Fountain

Replaced Drinking Fountain / awaiting test results

Brick Rancher	Basement Laundry Sink

Replaced Faucet and piping / Re-tested and Passed at 10.6 PPB

TO REDUCE EXPOSURE TO LEAD IN DRINKING WATER:

- Run your water to flush out lead: If water hasn’t been used for several hours, run water for 15 to 30 seconds or until it becomes cold or reaches a steady temperature before using it for drinking or cooking.

- Use cold water for cooking and preparing baby formula: Lead from the plumbing dissolves more easily into hot water.

Please note that boiling the water will not reduce lead levels.

ADDITIONAL INFORMATION

- For additional information, please contact William H. McCubbin Jr. at 410-444-5000 X 1237. For additional information on reducing lead exposure around your home/building and the health effects of lead, visit EPA’s website at www.epa.gov/lead. If you are concerned about exposure; contact your local health department or healthcare provider to find out how you can get your child tested for lead.