Lead in Drinking Water – Public and Nonpublic Schools

Updated in response to legislation effective as of June 1, 2021

IMPORTANT NOTICE:  ELEVATED LEAD WATER SAMPLE RESULT(S)

The Maryland School for the Blind

ACTION LEVEL (AL)

All Maryland public and nonpublic schools are required to sample all drinking water outlets for the presence of lead pursuant to the Code of Maryland Regulations (COMAR).

Effective June 1, 2021, the State’s Action Level (AL) for lead in drinking water outlet samples collected from sinks and water fountains in school buildings was lowered from 20 ppb (parts per billion) to 5 ppb. The AL is the concentration of lead, which, if exceeded, triggers required remediation of drinking water outlets.

ELEVATED LEAD WATER SAMPLE RESULT(S)

At previous testing conducted on 3/23/19, a total of 230 water-testing samples were collected from the Autism Learning Activities Center, Brick Rancher, Knefely Gymnasium, Multiple Disabilities Blind Center, Preschool/Early Learning Center, Outreach, Randall dorm, Sippel Pool, and Thompson dorm.

Of these testing samples, 60 had levels of lead exceeding the State’s revised AL of 5 parts per billion (ppb) for lead in drinking water in school buildings. The elevated lead results from the sample(s) collected at the above-mentioned buildings are listed in APPENDIX A below.

HEALTH EFFECTS OF LEAD

Lead can cause serious health problems if too much enters your body from drinking water or other sources. It can cause damage to the brain and kidneys and interfere with the production of red blood cells that carry oxygen to all parts of your body. The greatest risk of lead exposure is to infants, young children, and pregnant women. Lead is stored in the bones and can be released later in life. During pregnancy, the fetus receives lead from the mother’s bones, which may affect brain development. Scientists have linked the effects of lead on the brain with lowered IQ in children. Adults with kidney problems and high blood pressure have increased health risks associated with increased lead levels compared to healthy adults.

SOURCES OF HUMAN EXPOSURE TO LEAD

There are numerous sources of human exposure to lead. These sources include lead-based paint, lead-contaminated dust or soil, some plumbing materials, certain types of pottery, pewter, brass fixtures, food, cosmetics, certain hobbies, brass faucets, fittings, and valves.

According to the Environmental Protection Agency (EPA), 10 to 20 percent of a person’s potential exposure to lead may come from drinking water. An infant consuming formula mixed with lead-containing water may increase their exposure to 40 to 60 percent.

IMMEDIATE ACTIONS TAKEN

MSB has followed all immediate actions required by the Maryland Department of the Environments guidelines.

4 of the 60 outlets in question are designated as consumption water outlets (CO) and have been turned off while testing and remediation is performed. 24 outlets are designated as non-consumption water outlets (NC), and temporary signs have been placed for hand washing only and will be evaluated for remedial actions or possibly for permanent signage to be put in place. The remaining 32 outlets are dormitory bathroom sinks located within dorm rooms used for brushing teeth. After further review by MDE, these outlets have been reclassified as (CO) outlets. Per MDE recommendations, these outlets can remain accessible with handwashing only signs while remediation is taking place and bottled water supplied for brushing teeth.

NEXT STEPS

MSB is reviewing the list of fixtures and will replace fixtures, explore permanent signage options for non-consumption outlets, retest, and ensure lead levels are below the new 5 PPB standard set by MDE for all designated consumption outlets. Additionally, all required reporting will be followed as outlined in the MDE guidance.

TO REDUCE EXPOSURE TO LEAD IN DRINKING WATER:

- Run your water to flush out lead. If water hasn’t been used for several hours, run water for 15 to 30 seconds or until it becomes cold or reaches a steady temperature before using it for drinking or cooking.

- Use cold water for cooking and preparing baby formula. If lead is present in plumbing, it leaches more easily in hot water. Please note that boiling the water will not reduce lead levels.

ADDITIONAL INFORMATION

For additional information, please contact William H. McCubbin Jr., Director of Campus Operations, at 410-444-5000 Ext. 1237.

For information on reducing lead exposure around your home/building and the health effects of lead, visit the EPA’s website at www.epa.gov/lead.

If you are concerned about exposure, contact your local health department or healthcare provider to find out how to obtain a test.

APPENDIX A:  Testing results from 3/23/19

| OUTLET LOCATION | USE | Immediate Action | AL PPB |
| --- | --- | --- | --- |
| AUTISM LAC |  |  |  |
| Room 015 bathroom sink | NC | Signage/review | 10.6 |
| Room 108 bathroom middle sink | NC | Signage/review | 5.6 |
| 1st floor East girl’s Lavatory middle sink | NC | Signage/review | 9.5 |
| 1st floor East girl’s Lavatory right sink | NC | Signage/review | 7.4 |
| BRICK RANCHER |  |  |  |
| 1st bathroom on the right (sink) | CO | Signage/remediate | 7.1 |
| Basement laundry sink | NC | Signage/review | 10.6 |
| KNEFELY |  |  |  |
| Room 110 bathroom left sink | NC | Signage/review | 14.6 |
| Room 110 bathroom middle sink | NC | Signage/review | 16.6 |
| Room 110 bathroom right sink | NC | Signage/review | 13.3 |
| Room 109 bathroom left sink | NC | Signage/review | 15.3 |
| Room 109 bathroom middle sink | NC | Signage/review | 19.8 |
| Room 109 bathroom right sink | NC | Signage/review | 13.5 |
| Room 06 bathroom sink | NC | Signage/review | 17.5 |
| Room 07 bathroom sink | NC | Signage/review | 11.7 |
| MDB COTTAGES |  |  |  |
| Room 133 bathroom sink (Room 134 side) | NC | Signage/review | 6.1 |
| PRESCHOOL |  |  |  |
| Room 117 kitchen hand sink | CO | Signage/remediate | 11.6 |
| RANDALL |  |  |  |
| Room W2 bathroom sink | CO | Signage/remediate | 7.6 |
| Room W5 bathroom sink left (shared with W3) | CO | Signage/remediate | 13.4 |
| Room W5 bathroom sink right (shared with W3) | CO | Signage/remediate | 11.6 |
| C-7 drinking fountain | CO | Close/remediate | 6.6 |
| Room W11 bathroom sink left (shared with W9) | CO | Signage/remediate | 12.0 |
| Room E5 bathroom sink left (shared with E3) | CO | Signage/remediate | 5.8 |
| Room E5 bathroom sink right (shared with E3) | CO | Signage/remediate | 7.3 |
| Room W8 bathroom sink left (shared with W6) | CO | Signage/remediate | 6.3 |
| Room E14 bathroom sink right (shared with E12) | CO | Signage/remediate | 11.3 |
| Room E11 bathroom sink left (shared with E9) | CO | Signage/remediate | 8.1 |
| Room E11 bathroom sink right (shared with E9) | CO | Signage/remediate | 6.5 |
| Room E8 bathroom sink right (shared with E6) | CO | Signage/remediate | 8.0 |
| Room C1 bathroom sink | CO | Signage/remediate | 6.8 |
| SIPPEL |  |  |  |
| Main entrance drinking fountain | C | Close/remediate | 12.6 |
| (Girl’s restroom from left to right A sink) | NC | Signage/review | 17.9 |
| (Girl’s restroom from left to right B sink) | NC | Signage/review | 10.1 |
| (Girl’s restroom from left to right C sink) | NC | Signage/review | 6.8 |
| (Girl’s restroom from left to right D sink) | NC | Signage/review | 13.5 |
| (Girl’s restroom from left to right E sink) | NC | Signage/review | 11.8 |
| (Boy’s restroom from left to right A sink) | NC | Signage/review | 5.5 |
| (Boy’s restroom from left to right B sink) | NC | Signage/review | 9.8 |
| (Boy’s restroom from left to right C sink) | NC | Signage/review | 6.8 |
| (Boy’s restroom from left to right D sink) | NC | Signage/review | 7.1 |
| (Boy’s restroom from left to right E sink) | NC | Signage/review | 19.2 |
| THOMPSON |  |  |  |
| Room W6 bathroom sink left (shared with W4) | CO | Signage/remediate | 12.6 |
| Room W6 bathroom sink right (shared with W4) | CO | Signage/remediate | 9.1 |
| Room W9 bathroom sink left (shared with W7) | CO | Signage/remediate | 18.7 |
| Room W9 bathroom sink right (shared with W7) | CO | Signage/remediate | 6.8 |
| Room C11 bathroom sink | CO | Signage/remediate | 11.3 |
| Room C2 bathroom sink | NC | Signage/review | 8.4 |
| Room C4A kitchen sink left (next to entrance door) | CO | Close/remediate | 10.2 |
| Room C4 kitchen sink (dining area) | CO | Close/remediate | 5.5 |
| Room C5 bathroom sink | NC | Signage/review | 5.8 |
| Room C6 bathroom sink | NC | Signage/review | 7.4 |
| Room C8 laundry tray | NC | Signage/review | 16.0 |
| Room W3 bathroom left sink (shared with W1) | CO | Signage/remediate | 12.7 |
| Room W3 bathroom right sink (shared with W1) | CO | Signage/remediate | 8.1 |
| Room E12 bathroom left sink (shared with E10) | CO | Signage/remediate | 7.0 |
| Room E9 bathroom right sink (shared with E7) | CO | Signage/remediate | 8.3 |
| Room C7 bathroom sink | NC | Signage/review | 13.2 |
| Room E3 bathroom left sink (shared with E1) | CO | Signage/remediate | 5.6 |
| Room E3 bathroom right sink (shared with E1) | CO | Signage/remediate | 6.9 |
| Room E6 bathroom left sink (shared with E4) | CO | Signage/remediate | 17.1 |
| Room E6 bathroom right sink (shared with E4) | CO | Signage/remediate | 17.1 |